## Slide 1: Magnetic Noise Mitigation: Results obtained so far
AdV Weekly Meeting VIR-0016A-16

## Slide 2: Magnetic coupling
Sept. 2014 (AdV DIM VIR-0441A-14):
Outline of relevant “magnetic” problems we had in Virgo and how to avoid them
(new UPS system, new cabling architecture, toroidal transformers...)
Story begun in 2007
(DF coupling with CEB UPS Mains supply, L-room lights wiring problems …)

## Slide 3: Very short reminder
Sources Actuators Paths
typically only
one source:
Mains Supply (UPS)
Cables
Transformers
Non-zero area
of mains wires
Transformers
leakage
magnetic noise coupling to environment:

## Slide 4: SOURCE: UPS vs IPS noise
Mains noise and magnetic noise in the CEB (typical) during an UPS switch-off test (eLog 25397 and VIR-0737B-09 F. Nocera, F. Paoletti)
voltage mag. field mag. field
Time
Hz
Hz
(IPS is ~10 times less noisier than old UPS)
Solution: use “quieter” UPS

## Slide 5: Uninterruptible Power Supply
Basic UPS block diagram
Critical point is the INVERTER, basically a “Power-DAC” that re-build the 50Hz AC Mains from DC (can be “noisy”)

## Slide 6: ACTUATORS/PATH: transformers
Solution:
use toroidal transformers wherever possible
(~10 times smaller stray field)
Green: typical EI-shape transformer
Blue: same power but toroidal
Black: power off (noise floor)
tests with vacuum equipment transformers, Aug. 2012, VIR-0289A-12

## Slide 7: ACTUATORS/PATH: mains cables
Solution:
use twisted mains wires wherever possible
(~10 times smaller stray field)
Blue: standard wire
Red: twisted wire
D.Vander-Hyde (summer student) et al. VIR-0349A-13

## Slide 8: Searching for a “quieter” UPS
28 April 2015: measurements at a factory
(Chloride - Emerson Network Power) testing a low-noise UPS

## Slide 9: Searching for a “quieter” UPS
We had only small sharp lines around 6kHz (chopping frequency) where the new UPS was noisier (-50dB relative to 50Hz mains)

## Slide 10: The last Christmas shutdown
Most of the works done in CEB during Christmas holidays
- Recabling Mains with Twisted pair cables
- Switch to the new UPS
- Removal of power cables from floor trenches around towers and re-routing
(see VIR-0338B-13)

## Slide 11: Sources mitigation
Other works carried out in late 2015: power supplies nearby towers equipped with toroidal transformers
SLED and Optical Lever power supply
Vacuum racks transformers
(VIR-0289A-12)

## Slide 12: Results (at last!)
CEB magnetic field in different locations
(purple: before, black: after)

## Slide 13: Results (at last!)
Magnetic Budget (preliminary) – details in eLog 33093
….. all on before
___ all on now
___ UPS off
Good result: magnetic noise from UPS is now at the level of IPS

## Slide 14: Concerns …
Some mag. lines @ 6kHz worse than before
… maybe a notch filter ?
(we’re in contact with UPS tech. staff)
10nF
70mH
250 Ω
Q ~10
Worst case: 100 times higher mag. field, but mirrors displ. drops 1/ω³

## Slide 15: Conclusions
A lot of work done, by many people*
Good results! But:
not all devices are actually running in Virgo
+
environmental sensors still in temporary config./place
+
unknown situation @ NEB, WEB, MCB
=
repeat measurements in near future
*among many others: F. Carbognani, M. D’Andrea, I. Fiori, all the EGO Electronic group, D.Vander-Hyde ...

## Slide 16: Thank you